## Financial Summary
Financial Screening Summary
Solar PV Plant — 50 MW — Solar PV (Utility-Scale)
Generated: 2026-03-08 23:36:12
Project Assessment
Project Name | Solar PV Plant — 50 MW
Technology | Solar PV (Utility-Scale)
Capacity (MW) | 50
Capacity Factor | 22.0%
CAPEX (USD) | $45,000,000
Annual OPEX (USD) | $650,000
Project Life (years) | 25
Discount Rate | 8.0%
LCOE (USD/MWh) | $53.91
Project NPV (USD) | $10,967,700
Equity NPV (USD) | $16,949,798
FIRR (Project) | 10.66%
EIRR (Economic) | 12.53%
Simple Payback (years) | 8.8
Discounted Payback (years) | 15.5
Benefit-Cost Ratio | 1.178
Equity IRR | 17.52%
Minimum DSCR | 1.52
Average DSCR | 1.61
LLCR | 1.60

## Assumptions
Project Assumptions
Input parameters for financial analysis
Generated: 2026-03-08 23:36:12
General
Project Name | Solar PV Plant — 50 MW
Technology | Solar PV (Utility-Scale)
Capacity (MW) | 50
Capacity Factor | 22.0%
Annual Generation (MWh) | 96,360
Project Life (years) | 25
Cost Parameters
Total CAPEX (USD) | $45,000,000
Annual OPEX (USD) | $650,000
Modules & Inverters | $25,000,000
Balance of System | $10,000,000
Engineering & Development | $5,000,000
Contingency | $5,000,000
Financial Parameters
Discount Rate | 8.0%
Inflation Rate | 2.0%
Degradation Rate | 0.50%
Electricity Price (USD/MWh) | $65.00
Price Escalation | 1.5%
Debt Fraction | 70%
Debt Interest Rate | 6.0%
Debt Term (years) | 15
Tax Rate | 20%

## Cash Flow
Annual Cash Flow Analysis
Solar PV Plant — 50 MW — 25 year projection
Generated: 2026-03-08 23:36:12
Year | Generation (MWh) | Electricity Price | Revenue | OPEX | Total Costs | Project Cost Basis | Debt Service | Interest | Principal Repayment | CFADS | Depreciation | Project Tax | Equity Tax | Net Cash Flow | Economic Cash Flow | Equity Cash Flow | Outstanding Debt | DSCR | Cumulative Cash Flow | Discounted CF | Cumulative Discounted CF
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -45000000 | -45000000 | -13500000 | 31500000 |  | -45000000 | -45000000 | -45000000
1 | 96360 | 65 | 6263400 | 650000 | 4566007.06 | 1322680 | 3243327.06 | 1890000 | 1353327.06 | 4940720 | 2250000 | 672680 | 294680 | 4940720 | 5613400 | 2075392.94 | 30146672.94 | 1.523 | -40059280 | 4574740.74 | -40425259.26
2 | 95878 | 65.97 | 6325564.24 | 663000 | 4588839.91 | 1345512.85 | 3243327.06 | 1808800.38 | 1434526.69 | 4980051.4 | 2250000 | 682512.85 | 320752.77 | 4980051.4 | 5662564.24 | 2098484.41 | 28712146.25 | 1.535 | -35079228.6 | 4269591.39 | -36155667.87
3 | 95399 | 66.96 | 6388345.47 | 676260 | 4612004.16 | 1368677.09 | 3243327.06 | 1722728.77 | 1520598.29 | 5019668.38 | 2250000 | 692417.09 | 347871.34 | 5019668.38 | 5712085.47 | 2120887.07 | 27191547.96 | 1.548 | -30059560.23 | 3984774.6 | -32170893.27
4 | 94922 | 67.97 | 6451749.8 | 689785.2 | 4635505.18 | 1392178.12 | 3243327.06 | 1631492.88 | 1611834.19 | 5059571.68 | 2250000 | 702392.92 | 376094.34 | 5059571.68 | 5761964.6 | 2142543.19 | 25579713.77 | 1.56 | -24999988.55 | 3718936.23 | -28451957.05
5 | 94447 | 68.99 | 6515783.42 | 703580.9 | 4659348.47 | 1416021.41 | 3243327.06 | 1534782.83 | 1708544.24 | 5099762.01 | 2250000 | 712440.5 | 405483.94 | 5099762.01 | 5812202.51 | 2163391.51 | 23871169.53 | 1.572 | -19900226.54 | 3470812.33 | -24981144.72
6 | 93975 | 70.02 | 6580452.57 | 717652.52 | 4683539.6 | 1440212.53 | 3243327.06 | 1432270.17 | 1811056.89 | 5140240.04 | 2250000 | 722560.01 | 436105.97 | 5140240.04 | 5862800.04 | 2183367 | 22060112.64 | 1.585 | -14759986.5 | 3239223.15 | -21741921.57
7 | 93505 | 71.07 | 6645763.56 | 732005.57 | 4708084.23 | 1464757.17 | 3243327.06 | 1323606.76 | 1919720.31 | 5181006.39 | 2250000 | 732751.6 | 468030.25 | 5181006.39 | 5913757.99 | 2202400.68 | 20140392.33 | 1.597 | -9578980.12 | 3023067.47 | -18718854.1
8 | 93038 | 72.14 | 6711722.76 | 746645.68 | 4732988.16 | 1489661.1 | 3243327.06 | 1208423.54 | 2034903.52 | 5222061.66 | 2250000 | 743015.42 | 501330.71 | 5222061.66 | 5965077.08 | 2220419.31 | 18105488.81 | 1.61 | -4356918.45 | 2821317.43 | -15897536.68
9 | 92572 | 73.22 | 6778336.61 | 761578.6 | 4758257.26 | 1514930.2 | 3243327.06 | 1086329.33 | 2156997.74 | 5263406.41 | 2250000 | 753351.6 | 536085.74 | 5263406.41 | 6016758.01 | 2237345.21 | 15948491.07 | 1.623 | 906487.96 | 2633013.62 | -13264523.06
10 | 92110 | 74.32 | 6845611.6 | 776810.17 | 4783897.52 | 1540570.46 | 3243327.06 | 956909.46 | 2286417.6 | 5305041.14 | 2250000 | 763760.29 | 572378.39 | 5305041.14 | 6068801.43 | 2253095.97 | 13662073.47 | 1.636 | 6211529.1 | 2457260.51 | -10807262.54
11 | 91649 | 75.44 | 6913554.3 | 792346.37 | 4809915.02 | 1566587.96 | 3243327.06 | 819724.41 | 2423602.66 | 5346966.34 | 2250000 | 774241.58 | 610296.7 | 5346966.34 | 6121207.92 | 2267584.16 | 11238470.82 | 1.649 | 11558495.44 | 2293222.21 | -8514040.33
12 | 91191 | 76.57 | 6982171.32 | 808193.3 | 4836315.97 | 1592988.9 | 3243327.06 | 674308.25 | 2569018.82 | 5389182.42 | 2250000 | 784795.6 | 649933.95 | 5389182.42 | 6173978.02 | 2280717 | 8669452 | 1.662 | 16947677.85 | 2140118.49 | -6373921.85
13 | 90735 | 77.72 | 7051469.37 | 824357.17 | 4863106.67 | 1619779.61 | 3243327.06 | 520167.12 | 2723159.94 | 5431689.76 | 2250000 | 795422.44 | 691389.02 | 5431689.76 | 6227112.21 | 2292396.12 | 5946292.06 | 1.675 | 22379367.62 | 1997221.05 | -4376700.79
14 | 90281 | 78.88 | 7121455.21 | 840844.31 | 4890293.55 | 1646966.49 | 3243327.06 | 356777.52 | 2886549.54 | 5474488.72 | 2250000 | 806122.18 | 734766.67 | 5474488.72 | 6280610.9 | 2302517.16 | 3059742.51 | 1.688 | 27853856.34 | 1863850.13 | -2512850.66
15 | 89830 | 80.06 | 7192135.65 | 857661.2 | 4917883.15 | 1674556.09 | 3243327.06 | 183584.55 | 3059742.51 | 5517579.56 | 2250000 | 816894.89 | 780177.98 | 5517579.56 | 6334474.45 | 2310969.41 | 0 | 1.701 | 33371435.9 | 1739371.19 | -773479.47
16 | 89381 | 81.27 | 7263517.59 | 874814.42 | 1702555.05 | 1702555.05 | 0 | 0 | 0 | 5560962.54 | 2250000 | 827740.64 | 827740.64 | 5560962.54 | 6388703.18 | 5560962.54 | 0 |  | 38932398.44 | 1623191.96 | 849712.48
17 | 88934 | 82.48 | 7335608.01 | 892310.71 | 1730970.17 | 1730970.17 | 0 | 0 | 0 | 5604637.84 | 2250000 | 838659.46 | 838659.46 | 5604637.84 | 6443297.3 | 5604637.84 | 0 |  | 44537036.28 | 1514759.59 | 2364472.07
18 | 88489 | 83.72 | 7408413.92 | 910156.92 | 1759808.32 | 1759808.32 | 0 | 0 | 0 | 5648605.6 | 2250000 | 849651.4 | 849651.4 | 5648605.6 | 6498256.99 | 5648605.6 | 0 |  | 50185641.87 | 1413558.07 | 3778030.14
19 | 88047 | 84.98 | 7481942.42 | 928360.06 | 1789076.53 | 1789076.53 | 0 | 0 | 0 | 5692865.89 | 2250000 | 860716.47 | 860716.47 | 5692865.89 | 6553582.36 | 5692865.89 | 0 |  | 55878507.76 | 1319105.71 | 5097135.85
20 | 87606 | 86.25 | 7556200.7 | 946927.26 | 1818781.95 | 1818781.95 | 0 | 0 | 0 | 5737418.75 | 2250000 | 871854.69 | 871854.69 | 5737418.75 | 6609273.44 | 5737418.75 | 0 |  | 61615926.52 | 1230952.91 | 6328088.75
21 | 87168 | 87.55 | 7631196 | 965865.81 | 2298931.84 | 2298931.84 | 0 | 0 | 0 | 5332264.15 | 0 | 1333066.04 | 1333066.04 | 5332264.15 | 6665330.19 | 5332264.15 | 0 |  | 66948190.67 | 1059284.92 | 7387373.67
22 | 86732 | 88.86 | 7706935.62 | 985183.12 | 2329533.62 | 2329533.62 | 0 | 0 | 0 | 5377401.99 | 0 | 1344350.5 | 1344350.5 | 5377401.99 | 6721752.49 | 5377401.99 | 0 |  | 72325592.66 | 989122.05 | 8376495.72
23 | 86299 | 90.19 | 7783426.95 | 1004886.79 | 2360594.82 | 2360594.82 | 0 | 0 | 0 | 5422832.13 | 0 | 1355708.03 | 1355708.03 | 5422832.13 | 6778540.17 | 5422832.13 | 0 |  | 77748424.79 | 923591.2 | 9300086.92
24 | 85867 | 91.54 | 7860677.46 | 1024984.52 | 2392123.11 | 2392123.11 | 0 | 0 | 0 | 5468554.35 | 0 | 1367138.59 | 1367138.59 | 5468554.35 | 6835692.94 | 5468554.35 | 0 |  | 83216979.15 | 862387.4 | 10162474.32
25 | 85438 | 92.92 | 7938694.69 | 1045484.21 | 2424126.31 | 2424126.31 | 0 | 0 | 0 | 5514568.38 | 0 | 1378642.1 | 1378642.1 | 5514568.38 | 6893210.48 | 5514568.38 | 0 |  | 88731547.53 | 805225.72 | 10967700.04

## LCOE Analysis
Levelized Cost of Electricity (LCOE)
LCOE = PV(Total Costs) / PV(Total Generation)
Generated: 2026-03-08 23:36:12
LCOE Breakdown
LCOE (USD/MWh) | $53.91
PV of Total Costs (USD) | $53,238,123
PV of CAPEX (USD) | $45,000,000
PV of OPEX (USD) | $8,238,123
PV of Total Generation (MWh) | 987,611
LCOE — CAPEX Component (USD/MWh) | $45.56
LCOE — OPEX Component (USD/MWh) | $8.34

## Sensitivity LCOE
Sensitivity Analysis — LCOE
One-at-a-time parameter variation impact
Generated: 2026-03-08 23:36:12
| -20% | -10% | +0% | +10% | +20% | 0.05 | 0.06 | 0.08 | 0.1 | 0.12 | 45 | 55 | 65 | 75 | 85 | 0.18 | 0.2 | 0.22 | 0.24 | 0.26
CAPEX | 44.79 | 49.35 | 53.91 | 58.46 | 63.02
Discount Rate | [5 empty] | 43.36 | 46.73 | 53.91 | 61.56 | 69.61
Electricity Price | [10 empty] | 53.91 | 53.91 | 53.91 | 53.91 | 53.91
Capacity Factor | [15 empty] | 65.89 | 59.3 | 53.91 | 49.41 | 45.61
Annual OPEX | 52.24 | 53.07 | 53.91 | 54.74 | 55.57

## Sensitivity NPV
Sensitivity Analysis — NPV
One-at-a-time parameter variation impact
Generated: 2026-03-08 23:36:12
| -20% | -10% | +0% | +10% | +20% | 0.05 | 0.06 | 0.08 | 0.1 | 0.12 | 45 | 55 | 65 | 75 | 85 | 0.18 | 0.2 | 0.22 | 0.24 | 0.26
CAPEX | 19084066.78 | 15025883.41 | 10967700.05 | 6909516.68 | 2851333.31
Discount Rate | [5 empty] | 29442698.87 | 22350887.82 | 10967700.05 | 2371512.26 | -4243547.51
Electricity Price | [10 empty] | -6921540.67 | 2023079.69 | 10967700.05 | 19912320.4 | 28856940.75
Capacity Factor | [15 empty] | 396785.06 | 5682242.55 | 10967700.05 | 16253157.53 | 21538615.01
Annual OPEX | 12285799.77 | 11626749.92 | 10967700.05 | 10308650.18 | 9649600.32

## Sensitivity IRR
Sensitivity Analysis — IRR
One-at-a-time parameter variation impact
Generated: 2026-03-08 23:36:12
| -20% | -10% | +0% | +10% | +20% | 0.05 | 0.06 | 0.08 | 0.1 | 0.12 | 45 | 55 | 65 | 75 | 85 | 0.18 | 0.2 | 0.22 | 0.24 | 0.26
CAPEX | 0.1356 | 0.1197 | 0.1066 | 0.0955 | 0.086
Discount Rate | [5 empty] | 0.1066 | 0.1066 | 0.1066 | 0.1066 | 0.1066
Electricity Price | [10 empty] | 0.0617 | 0.0851 | 0.1066 | 0.1269 | 0.1463
Capacity Factor | [15 empty] | 0.081 | 0.0941 | 0.1066 | 0.1187 | 0.1305
Annual OPEX | 0.1096 | 0.1081 | 0.1066 | 0.1051 | 0.1036

## Sensitivity EIRR
Sensitivity Analysis — EIRR
One-at-a-time parameter variation impact
Generated: 2026-03-08 23:36:12
| -20% | -10% | +0% | +10% | +20% | 0.05 | 0.06 | 0.08 | 0.1 | 0.12 | 45 | 55 | 65 | 75 | 85 | 0.18 | 0.2 | 0.22 | 0.24 | 0.26
CAPEX | 0.1599 | 0.1409 | 0.1253 | 0.1122 | 0.101
Discount Rate | [5 empty] | 0.1253 | 0.1253 | 0.1253 | 0.1253 | 0.1253
Electricity Price | [10 empty] | 0.0726 | 0.1 | 0.1253 | 0.1494 | 0.1727
Capacity Factor | [15 empty] | 0.0952 | 0.1105 | 0.1253 | 0.1397 | 0.1537
Annual OPEX | 0.1289 | 0.1271 | 0.1253 | 0.1235 | 0.1218

## Tornado Data
Tornado Chart Data — NPV Sensitivity
Generated: 2026-03-08 23:36:12
Parameter | Min | Max | Range | Base
Annual OPEX | 9649600.32 | 12285799.77 | 2636199.45 | 10967700.05
CAPEX | 2851333.31 | 19084066.78 | 16232733.47 | 10967700.05
Capacity Factor | 396785.06 | 21538615.01 | 21141829.95 | 10967700.05
Discount Rate | -4243547.51 | 29442698.87 | 33686246.38 | 10967700.05
Electricity Price | -6921540.67 | 28856940.75 | 35778481.42 | 10967700.05